## Slide 1: Basic Wastewater Math
NMWWA Central Short School
"Fred Ragsdale Memorial" School
Albuquerque, NM
September 8 – 11, 2025

## Slide 2: Conversion/Formula Sheet
Corrections
How to use portions of the document

## Slide 3: Conversions
Utilizing conversions
Changes units but not magnitude
Essentially multiplication by “1”
Important to include units
3
3
12in
1 ft
=
1
=
1ft__
12 in
=
=
1

## Slide 4: 1. Convert 3.2 miles to feet
Find the correct conversion factor (Page 3)
1 mile = 5,280 ft
x
5,280 ft. 1 mile
3.2 miles 1
16,896 ft.
=

## Slide 5: 2. 3.2 acres to sq.ft.
Find the correct conversion factor (Page 1)
1 acre = 43,560 ft2
x
43,560 ft.2 1 acres
3.2 acres 1
139,392 ft.2
=

## Slide 6: 3. 678,754 cu.ft. to acre-ft.
Find the correct conversion factor (Page 1)
1 acre-ft = 43,560 ft3
x
1 ac-ft__ 43,560 ft.3
678,754 ft3 1
15.58 ac-ft.
=

## Slide 7: 4. 3.7 MGD to gpm
Find the correct conversion factor (Page 3)
1 MGD = 694.4 gpm
x
694.4 gpm 1 MGD
3.7 MGD 1
2,569.3 gpm
=

## Slide 8: 5. 1,250 gpm to cfs
Find the correct conversion factor (Page 3)
1 ft3/sec = 449 gpm
x
1 ft3/sec_ 449 gpm
1,250 gpm 1
2.78 ft3/sec
=

## Slide 9: 6. 0.9 cfs to MGD
Find the correct conversion factor (Page 3)
1 ft3/sec = 0.6463 MGD or 1 MGD = 1.547 cfs
x
0.6463 MGD 1 ft3/sec
0.9 ft3/sec 1
0.58 MGD
=

## Slide 10: 7. 768 gpm to acre-ft/day
Find the correct conversion factor (Page 3)
1 MGD = 3.07 acre-ft/day and 1 MGD = 694.4gpm
x
1 MGD__ 694.4 gpm
768 gpm 1
3.4 ac-ft/day
=
x
3.07ac-ft/day 1 MGD

## Slide 11: 8. 5.6 MGD to cfs
Find the correct conversion factor (Page 3)
1 ft3/sec = 0.6463 MGD or 1 MGD = 1.547 cfs
x
1 ft3/sec___ 0.6463 MGD
5.6 MGD 1
8.66 ft3/sec
=
1.547 ft3/sec
1 MGD
x
8.66 ft3/sec
=

## Slide 12: 9. 25ºC to ºF
Find the correct formula (Page 10)
°F = (°C x 1.8) + 32
x
1.8)
(25ºC
77⁰F
=
+
32

## Slide 13: 10. 90ºF to ºC
Find the correct formula (Page 10)
(°F – 32) x (0.556) (corrected)
x
32)
(90ºF
32.2⁰C
=
-
0.556

## Slide 14: 11. Determine the surface area (exposed water area) of a rectangular clarifier, in sq. ft., if the clarifier is 74 feet in length and 32 feet in width.
Find the correct formula (Page 4)

## Slide 16: Number 11 Calculation
Length (l) x Width (w)
32 ft.
74 ft.
2,368 ft2
=
x

## Slide 17: 12. A circular clarifier has a diameter of 72 feet and a depth of 31 feet. Determine the surface area (exposed water area) of the clarifier in sq. ft.
Find the correct formula (Page 4)

## Slide 19: Number 12 Calculation
0.785D2
0.785 x D x D
72 ft.
0.785
4,069 ft2
=
x
x
72 ft.

## Slide 20: 13. A trickling filter is 58 feet in diameter and has a media depth of 6 feet. Determine the surface area of the media of the trickling filter, in sq. ft.
Find the correct formula (Page 4)

## Slide 21: Number 13 Calculation
0.785D2
0.785 x D x D
58 ft.
0.785
2,641 ft2
=
x
x
58 ft.

## Slide 22: 14. A pond has a width of 380 feet and a length of 540 feet. Determine the surface area of the pond in acres.
Find the correct formula (Page 9)
A = [(L) x (W)]/ (43,560 ft2/ac)

## Slide 23: Number 14 Calculation
(Length (l) x Width (w))/(43,560 ft2/ac)
380 ft.)
(540 ft.
4.7 acres
=
x
÷
(43,560 ft2/acre)

## Slide 24: 15. Determine the cross-sectional area, in sq. ft., of the flow in a grit channel which is 2.5 feet in width and flowing to a depth of 1 foot, 3 inches.
Find the correct formula (Page 4)

## Slide 25: Number 15 Calculation
Length (l) x Width (w)
Step 1 is to convert to the same units.
1 ft. 3 inches = 1.25 ft.
1.25 ft.
2.5 ft.
3.1 ft2
=
x

## Slide 26: 16. Determine the cross-sectional area, in square inches, of a pipe which is 18 inches in diameter.
Find the correct formula (Page 4)

## Slide 27: Number 16 Calculation
0.785D2
0.785 x D x D
18 in.
0.785
254.34 sq.in.
=
x
x
18 in.

## Slide 28: 17. A rectangular clarifier is 58 feet in length, 24 feet in width, and 18 feet in depth. Determine the volume in cubic feet.
Find the correct formula (Page 4)

## Slide 30: Number 17 Calculation
Length (l) x Width (w) x Height (h)
24 ft.
58 ft.
25,056 ft3
=
x
x
18 ft.

## Slide 31: 18. A rectangular clarifier is 62 feet in length, 31 feet in width, and 24 feet in depth. Determine the volume in gallons.
Find the correct formula (Page 4)

## Slide 32: Number 18 Calculation
Length (l) x Width (w) x Height (h)
Cubic feet must be converted to gallons.
31 ft.
62 ft.
46,128 ft3
=
x
x
24 ft.
46,128 ft3 1
x
7.48 gals 1 ft3
=
345,037 gals

## Slide 33: 19. A circular clarifier is 71 feet in diameter and has a depth of 22 feet. Determine the volume of the clarifier in cubic feet.
Find the correct formula (Page 4)

## Slide 35: Number 19 Calculation
(0.785) x (D2) x (h)
0.785 x D x D x h
71 ft.
0.785
87,058 ft3
=
x
x
71 ft.
x
22 ft.

## Slide 36: 20. A circular clarifier is 64 feet in diameter and a depth of 22 feet. Determine the volume of the clarifier in million gallons.
Find the correct formula (Page 4)

## Slide 37: Number 20 Calculation
(0.785) x (D2) x (h)
0.785 x D x D x h
Cubic feet must be converted to million gallons
64 ft.
0.785
70,738 ft3 1
=
x
x
64 ft.
x
22 ft.
7.48 gals 1 ft3
x
70,738 ft3
x
1 MG_____ 1,000,000 gals
=
0.53 MG

## Slide 38: 21. A pond has a width of 272 feet, a length of 388 feet, and a depth of 6 feet. Determine the volume of the pond in cubic feet.
Find the correct formula (Page 4)

## Slide 39
Typical shape of ponds but for basic math only the surface area will be calculated.

## Slide 40: Number 21 Calculation
Length (l) x Width (w) x Height (h)
272 ft.
388 ft.
633,216 ft3
=
x
x
6 ft.

## Slide 41: 22. A pond has a width of 450 feet, a length of 675 feet, and a depth of 5 feet. Determine the volume of the pond in acre-feet.
Find the correct formula (Page 4 and
Page 1)

## Slide 42: Number 22 Calculation
Length (l) x Width (w) x Height (h)
Cubic feet must be converted to acre-ft
450 ft.
675 ft.
1,518,750 ft3
=
x
x
5 ft.
1,518,750 ft3 1
x
1 acre-foot 43,560 ft3
=
34.87 ac-ft

## Slide 43: 23. A grit channel is 24 feet in length and a stick that has been dropped into the channel travels the length of the channel in 32 seconds. Determine the velocity of flow in the channel.
Find the correct formula (Page 5)
V = (d)/(T)
24 ft__ 32 sec
=
0.75 ft/sec

## Slide 44: 24. Determine the flow rate, in cfs, in a channel that is 3 feet in width and flowing at a depth of 2 feet, and the velocity of flow is 2.0 feet per second.
Find the correct formula (Page 5)
Q = (w) x (d) x (V)

## Slide 45
ft3/sec
Page 4

## Slide 46: Number 24 Calculation
Q = (w) x (d) x (V)
2 ft.
3 ft.
12 ft3/sec
=
x
x
2 ft./sec

## Slide 47: 25. Determine the flow rate, in million gallons per day, in a channel that is 2 feet in width, 2 feet in depth, flowing half-full at a velocity of 0.9 feet per second.
Find the correct formula (Page 5)
Q = (w) x (d) x (V)

## Slide 48: Number 25 Calculation
Q = (w) x (d) x (V)
Cubic feet/sec must be converted to
MGD
1 ft.
2 ft.
1.8 ft3/sec
=
x
x
0.9 ft/sec
1.8 ft3/sec 1
x
0.646 MGD 1 ft3/sec
=
1.16 MGD

## Slide 49: 26. An 18-inch pipe is flowing full at a velocity of 2.1 feet per second. Determine the flow rate in cubic feet per second.
Find the correct formula (Page 5)
Q = (0.785) x (D)2 x (V)
V

## Slide 50: Number 26 Calculation
Q = (0.785) x (D)2 x (V)
Q = 0.785 x D x D x V
18 inches = 1.5 ft.
1.5 ft.
0.785
3.71 ft3/sec
=
x
x
2.1 ft./sec
1.5 ft.
x

## Slide 51: 27. A 24-inch pipe is flowing full at a velocity of 1.1 feet per second. Determine the flow rate in gallons per minute.
Find the correct formula (Page 5)
Q = (0.785) x (D)2 x (V)

## Slide 52: Number 27 Calculation
Q = (0.785) x (D)2 x (V)
Q = 0.785 x D x D x V
24 inches = 2 ft.
2 ft.
0.785
3.45 ft3/sec
=
x
x
1.1 ft./sec
2 ft.
x
3.45 ft3/sec 1
x
449 gpm__ 1 ft3/sec
=
1,549 gpm

## Slide 53: 28. Determine the detention time, in hours, for a rectangular clarifier that is 68 feet in length, 27 feet in width, and 18 feet in depth, if the flow into the clarifier is 2.6 MGD.
Find the correct formula (Page 11)

## Slide 54: Number 28 Calculation
27 ft.
68 ft
33,048 ft3
=
x
x
18 ft.
33,048 ft3 1
7.48 gal 1 ft3
x
=
247,199 gal
2.6 MGD = 2,600,000 gal/day

## Slide 55: Number 28 Calculation (cont.)
x
=
2,600,000 gal/day
24 hr./day
247,199 gal
2.3 hrs.

## Slide 56: 29. A rectangular clarifier is 65 feet in length, 23 feet in width, and has an operating depth of 17 feet. Determine the detention time, in hours, if the flow into the clarifier is 1.1 MGD.
Find the correct formula (Page 11)

## Slide 57: Number 29 Calculation
23 ft.
65 ft
25,415 ft3
=
x
x
17 ft.
25,415 ft3 1
7.48 gal 1 ft3
x
=
190,104 gal
1.1 MGD = 1,100,000 gal/day

## Slide 58: Number 29 Calculation (cont.)
x
=
1,100,000 gal/day
24 hr./day
190,104 gal
4.1 hrs.

## Slide 59: 30. Determine the detention time in a clarifier, in hours, that has a diameter of 62 feet and a depth of 21 feet, if the flow into the clarifier is 1.6 MGD.
Find the correct formula (Page 11)

## Slide 60: Number 30 Calculation
62 ft.
0.785
63,368 ft3
=
x
x
21 ft.
63,368 ft3 1
7.48 gal 1 ft3
x
=
473,993 gal
1.6 MGD = 1,600,000 gal/day
x
62 ft.

## Slide 61: Number 30 Calculation (cont.)
x
=
1,600,000 gal/day
24 hr./day
473,993 gal
7.1 hrs.

## Slide 62: 31. Determine the detention time in a clarifier, in hours, that has a diameter of 64 feet and a depth of 18 feet, if the flow into the clarifier is 1.5 MGD.
Find the correct formula (Page 11)

## Slide 63: Number 31 Calculation
64 ft.
0.785
57,876 ft3
=
x
x
18 ft.
57,876 ft3 1
7.48 gal 1 ft3
x
=
432,912 gal
1.5 MGD = 1,500,000 gal/day
x
64 ft.

## Slide 64: Number 31 Calculation (cont.)
x
=
1,500,000 gal/day
24 hr./day
432,912 gal
6.9 hrs.

## Slide 65: 32. Determine the detention time in a pond that has a surface area of 12.6 acres, a depth of 5 feet, and an average daily flow of 0.9 MGD.
Find the correct formula (Page 11 and Page 1)
DT = (V)/(Q)
  Detention time: days
  Volume: acre-ft
  Flow: acre-ft/day

## Slide 66: Number 32 Calculation
DT = (V)/(Q)
12.6 acres
63 ac-ft
=
x
x
0.9 MGD 1
3.07 ac-ft/day 1 MGD
=
2.6 ac-ft/day
5 ft.
63 ac-ft__ 2.6 ac-ft/day
24 days
=

## Slide 67: 33. Determine the detention time in a pond that has a surface area of 18 acres, a depth of 6 feet, and an average daily flow of 0.8 MGD.
Find the correct formula (Page 11 and Page 1)
DT = (V)/(Q)
  Detention time: days
  Volume: acre-ft
  Flow: acre-ft/day

## Slide 68: Number 33 Calculation
DT = (V)/(Q)
18 acres
108 ac-ft
=
x
x
0.8 MGD 1
3.07 ac-ft/day 1 MGD
=
2.5 ac-ft/day
6 ft.
108 ac-ft__ 2.5 ac-ft/day
43 days
=

## Slide 69: 34. Determine the surface overflow rate on a clarifier if the diameter of the clarifier is 62 feet in, the depth is 18 feet, and the average daily flow is 2.1 MGD.
Find the correct formula (Page 10 and Page 4)
Surface loading rate or Surface overflow rate = Flow
A

## Slide 70: Number 34 Calculation
62 ft.
0.785
3,018 ft2
=
x
2,100,000 gpd 3,018 ft2
=
696 gpd/ft2
2.1 MGD = 2,100,000 gal/day
x
62 ft.
Q, gpd Area, ft2

## Slide 71: 35. Determine the surface overflow rate on a clarifier if the diameter of the clarifier is 62 feet, the depth is 22 feet, and the average daily flow 1.3 MGD.
Find the correct formula (Page 10 and Page 4)
Surface loading rate or Surface overflow rate = Flow
A

## Slide 72: Number 35 Calculation
62 ft.
0.785
3,018 ft2
=
x
1,300,000 gpd 3,018 ft2
=
431 gpd/ft2
1.3 MGD = 1,300,000 gal/day
x
62 ft.
Q, gpd Area, ft2

## Slide 73: 36. Determine the hydraulic loading on a trickling filter if the trickling filter is 65 feet in diameter and is receiving a flow of 1.4 MGD.
Find the correct formula (Page 10 and Page 4)
Surface loading rate or Surface overflow rate = Flow
A

## Slide 74: Number 36 Calculation
65 ft.
0.785
3,317 ft2
=
x
1,400,000 gpd 3,317 ft2
=
422 gpd/ft2
1.4 MGD = 1,400,000 gal/day
x
65 ft.
Q, gpd Area, ft2

## Slide 75: 37. A trickling filter that is receiving 1.8 MGD is 74 feet in diameter and the media depth is 5 feet. What is the hydraulic loading?
Find the correct formula (Page 10 and Page 4)
Surface loading rate or Surface overflow rate = Flow
A

## Slide 76: Number 37 Calculation
74 ft.
0.785
4,299 ft2
=
x
1,800,000 gpd 4,299 ft2
=
419 gpd/ft2
1.8 MGD = 1,800,000 gal/day
x
74 ft.
Q, gpd Area, ft2

## Slide 77: 38. A pond receives an average daily flow of 0.9 MGD. The surface area of the pond is 64 acres. Determine the hydraulic loading on the pond in inches/day.
Find the correct formula (Page 9)
HLR = [(Q)/(A)] x 12 in/ft. = inches/day
Q: acre-ft/day
Area: acres

## Slide 78: Number 38 Calculation HLR = [(Q)/(A)] x 12 in/ft. = inches/day
=
x
=
0.53 in/day
0.9 MGD 1
3.07 ac-ft/day 1 MGD
2.8 ac-ft/day
[(2.8 ac-ft/day)
/
(64 acres)]
x
12 in/ft.

## Slide 79: 39. A pond is receiving 0.8 MGD. The pond has a surface area of 16 acres and a depth of 6 feet. What is the hydraulic loading in inches/day?
Find the correct formula (Page 9)
HLR = [(Q)/(A)] x 12 in/ft. = inches/day
Q: acre-ft/day
Area: acres

## Slide 80: Number 39 Calculation HLR = [(Q)/(A)] x 12 in/ft. = inches/day
=
x
=
1.9 in/day
0.8 MGD 1
3.07 ac-ft/day 1 MGD
2.5 ac-ft/day
[(2.5 ac-ft/day)
/
(16 acres)]
x
12 in/ft.

## Slide 81: 40. Determine the weir overflow rate for a clarifier that has a diameter of 62 feet and is receiving a flow of 1.9 MGD.
Find the correct formula (Page 5)
Overflow rate = (Q)/(L)
Circumference = (π) x (D)

## Slide 82: Number 40 Calculation
π
195 ft
=
x
1,900,000 gpd 195 ft
=
9,744 gpd/ft
1.9 MGD = 1,900,000 gal/day
62 ft.
Q, gpd__ Length, ft

## Slide 83: 41. The WWTP receives 2.1 MGD. The primary clarifier has a diameter of 78 feet and an operating depth of 18 feet. What is the weir overflow rate?
Find the correct formula (Page 5)
Overflow rate = (Q)/(L)
Circumference = (π) x (D)

## Slide 84: Number 41 Calculation
π
245 ft
=
x
2,100,000 gpd 245 ft
=
8,571 gpd/ft
2.1 MGD = 2,100,000 gal/day
78 ft.
Q, gpd__ Length, ft

## Slide 85: 42. Determine the population loading for a pond that receives 0.8 MGD, has a surface area of 22 acres, and serves a population of 4600 persons.
Find the correct formula (Page 9)
PL = (Population)/(A)

## Slide 86: Number 42 Calculation
4600 persons 22 acres
=
209 persons/acres
Population_ Acres

## Slide 87: 43. Determine the demand if the dosage applied to the flow is 2.8 mg/L and the residual is 1.1 mg/L.
Find the correct formula (Page 6)
Dose = Demand + Residual
Dose – Residual = Demand
2.8 mg/L
1.1 mg/L
1.7 mg/L
=
-

## Slide 88: 44. The desired chlorine residual is 0.9 mg/L and the demand is 2.3 mg/L. What is the dosage that should be applied to the wastewater to achieve the desired residual?
Find the correct formula (Page 6)
Dose = Demand + Residual
2.3 mg/L
0.9 mg/L
3.2 mg/L
=
+

## Slide 89: 45. Determine the feed rate, in pounds per day of chlorine gas, if the flow through the plant is 1.3 MGD and the dosage to maintain the desired residual is 4.2 mg/L.
Find the correct formula (Page 6)
Feed rate = (d) x (Q) x (8.34 lbs./gal)
4.2 mg/L
1.3 MGD
46 lbs./day
=
x
x
8.34 lbs./gal

## Slide 90: 46. The dosage required to maintain the desired residual is 4.1 mg/L. How many pounds per day, of gaseous chlorine, must be fed if the flow is 0.8 MGD?
Find the correct formula (Page 6)
Feed rate = (d) x (Q) x (8.34 lbs./gal)
4.1 mg/L
0.8 MGD
28 lbs./day (Explain the rounding)
=
x
x
8.34 lbs./gal

## Slide 91: 47. Determine the feed rate, in pounds per day, if the flow through the plant is 0.84 MGD, the required dosage is 3.4 mg/L, and you are applying HTH with an availability of 65%.
Find the correct formula (Page 6)
Feed rate = (d) x (Q) x (8.34 lbs./gal)
3.4 mg/L
0.84 MGD
37 lbs./day
=
x
x
8.34 lbs./gal
0.65
Chemical Purity

## Slide 92: 48. A WWTP is using 5% sodium hypochlorite to disinfect the effluent. If the required dosage is 4.1 mg/L and the flow 0.5 MGD, how many pounds per day will need to be fed to the flow?
Find the correct formula (Page 6)
Feed rate = (d) x (Q) x (8.34 lbs./gal)
4.1 mg/L
0.5 MGD
342 lbs./day
=
x
x
8.34 lbs./gal
0.05
Chemical Purity

## Slide 93: 49. The blower produces 300 cfm. The diameter of the manhole is 8 feet, and the depth is 15 feet. Determine the number of air exchanges per hour.
First determine the volume, in cf, for the manhole.
0.785 x (8ft.)2 x 15 ft. = 753.6 cf
Next: Determine the amount of air produced per hour by the blower.
300 cf x 60 min = 18,000 cf/hr
min hr

## Slide 94: 49. Calculation (cont.)
Next: Determine the exchange rate per hour.
18,000 cf/hr = 23.8 exchanges/hr
753.6 cf

## Slide 95: 50. What is the minimum cfm capacity of a blower if the desired air exchange is 20 exchanges per hour and the manhole has the following dimensions: 10 feet in diameter and 10 feet in depth?
First determine the volume, in cf, for the manhole.
0.785 x (10ft.)2 x 10 ft. = 785 cf
Next: Determine the cfm for the blower.
785 cf x 20 x __hr = 262 cfm
1 hr 60 min